## Logical Model
Entity | Entity Definition
Alert | An occurrence of a unfavorable condition of a Facility or Equipment Item that may require intervention in order to resume to full operation.
Alert Response | Contains the information necessary to understand the reaction or work performed to Alerts.
Alert Resolution | Contains the information necessary to understand how an Alert was resolved.
Alert Facility | Contains the speciifc Facility(s) that are related to Alerts.
Alert Equipment Item | Contains the speciifc Equipment Item(s) that are related to Alerts.
Alert Priority Type | The valid set of classifications for how an Alert is ranked in importance.
Alert Type | The valid set of classifications for Alerts.
Alert Type Priority Type | The valid set of Alert Types and its assigned Priority Type. Some Alert Types may be associated to more than 1 Priority Type.
Alert Sub Type | The high-level valid set of classifications for where the Alert occurred. Classifications are based on facility, material and process.
Alert Process Type | The valid set of classifications for the process for which the Alert occurred.
Alert Trigger Type | The valid set of classifications for how an Alert is reported.
Alert Triggering System | The valid list of system generated issues that create Alerts through automation.
Alert Resolution Type | The valid set of classifications for how an Alert is resolved.
Alert Response Type | The valid set of classifications of the reaction to an Alert.
Alert Likely Cause | The list of documented reasons an Alert may have occurred.
Alert Remediation | The list of documented resolutions for Alerts.
Alert Likely Cause Remediation | The association of an Alert Unlikely Cause and the Alert Remediation that resolved the unfavorable condition.
Alert Resolution Remediation | The link between an Alert Resolution and the Alert Remediation that fix the unfavorable condition.
Facility | A capability to perform a business function or a service. It is a token or a concept used to describe the functional capability that may arise from the installation of Equipment and Materials. Facilities do not have mass, they are not physical objects. Only the Equipment or Materials that are installed to provide the service are physical objects. The actual equipment or materials that are installed at a Facility can change over time, and can be any type of equipment or materials that carry out the same business function. Facilities enable business functions to be described independently of the equipment or materials that may be installed from time to time.
Management Plant | A type of facility that is the highest level facility in the facility structure of the enterprise. Management Plants contain all other facilities in the enterprise. They are used for management purposes of maintenance planning, reporting, etc.
Equipment Item | A manufactured, non consumable, and uniquely identifiable object that is of importance to the enterprise to track at the individual instance level. Examples of equipment include: a pump with an identification number, and a computer CPU with a serial number.
Facility Type | The definition of a kind of capability to perform a business function or a service.
Material Type | The definition of an object or good that is identified and measured by quantity, volume, or count. A Material Type may or may not be uniquely identifiable, but it is not tracked at the individual instance level, as it is not important to the enterprise to track these items at that level. Examples of MATERIAL TYPES include: oil, water, gas, computer keyboards, paper clips, 2-3/8" red band 4.7 lb/ft tubing, 2-7/8" yellow band 6.5 lb/ft tubing, Milwaukee size 3 cast iron 200 psig working pressure butterfly valve, John Crane 5611 1-3/4" Cartridge mount Mechanical Seal.
Completion Purpose Types | The definition of a kind of reason why a COMPLETION exists. That is, the intended purpose for a completion.
Worker | Anyone who provides a service to Aera. This is a role a person may play. Workers are either employees or contingent workers.
Entity | Attribute | Attribute Definition
Alert | Alert ID | The unique system-generated identifier for this instance of an ALERT.
Alert | Alert Create Date | The point in time when the ALERT was created.
Alert | Alert Creator Person Business Entity ID | The unique identifier for the specific PERSON that created, reviewed, and diagnosed this instance of an ALERT.
Alert | Alert Trigger Type ID | Identifies the means in which the ALERT was reported.
Alert | Alert Reported By Person Business Entity ID | The unique identifier for the specific PERSON that reported this instance of an ALERT.
Alert | Alert Triggering System ID | The unique identifier for the specific system that triggered this instance of an ALERT.
Alert | Alert Priority Type ID | The unique identifier for the specific PRIORITY related to this instance of a ALERT.
Alert | Alert Type ID | The unique identifier for the specific ALERT TYPE related to this instance of a ALERT.
Alert | Alert Description | A user provided description for each instance of an ALERT.
Alert Type | Alert Type ID | The unique system-generated identifier for this instance of an ALERT TYPE.
Alert Type | Alert Type Name | The unique textual designation given to this instance of an ALERT TYPE.
Alert Type | Alert Type Description | Text describing this instance of an ALERT TYPE.
Alert Type | Alert Sub Type ID | The unique identifier for the specific ALERT SUB TYPE that reported this instance of an ALERT TYPE.
Alert Type | Effective Date | The date and time this instance became active.
Alert Type | Termination Date | The last date that an instance of ALERT TYPE was valid
Alert Response | Alert Response ID | The unique system-generated identifier for this instance of an ALERT RESPONSE.
Alert Response | Alert ID | The unique identifier for the specific ALERT that reported this instance of an ALERT RESPONSE.
Alert Response | Response Type ID | The unique identifier for the specific RESPONSE TYPE that reported this instance of an ALERT RESPONSE.
Alert Response | Response Creator Business Entity ID | The unique identifier for the specific PERSON that created this instance of an ALERT RESPONSE.
Alert Response | Response Text | Textual description of work performed necessary to resolve the ALERT.
Alert Response | Response Create Date Time | The point in time when the ALERT RESPONSE was created.
Alert Response | Response Completion Date Time | The date the time the response activity/work was finished.
Alert Response | PM Number | The SAP expense number assigned to the work order created as a result of an ALERT.
Alert Response | Network Number | The SAP capital number assigned to the work order created as a result of an ALERT.
Alert Response | Network Activity Number | The SAP capital number's activity number assigned to the work order created as a result of an ALERT.
Alert Trigger Type | Alert Trigger Type ID | The unique system-generated identifier for this instance of an ALERT TRIGGER TYPE.
Alert Trigger Type | Alert Trigger Type Name | The unique textual designation given to this instance of an ALERT TRIGGER TYPE.
Alert Trigger Type | Effective Date | The date and time this instance became active.
Alert Trigger Type | Termination Date | The last date that an instance of ALERT TRIGGER TYPE was valid
Alert Triggering System | Alert Triggering System ID | The unique system-generated identifier for this instance of an ALERT TRIGGERING SYSTEM TRIGGER.
Alert Triggering System | Alert Triggering System Name | The unique textual designation given to this instance of an ALERT TRIGGERING SYSTEM TRIGGER.
Alert Triggering System | Alert Triggering System Description | Text describing this instance of an ALERT TRIGGERING SYSTEM TRIGGER.
Alert Triggering System | Effective Date | The date and time this instance became active.
Alert Triggering System | Termination date | The last date that an instance of ALERT SYSTEM TRIGGER TYPE was valid.
Alert Priority Type | Alert Priority Type ID | The unique system-generated identifier for this instance of an ALERT PRIORITY TYPE.
Alert Priority Type | Alert Priority Type Name | The unique textual designation given to this instance of an ALERT PRIORITY TYPE.
Alert Priority Type | Alert Priority Type Description | Text describing this instance of an ALERT PRIORITY TYPE.
Alert Priority Type | Standard Acknowledgement Hour Count | Indicates the standard maximum duration of time (in hours) that could pass prior to being reported for an ALERT for this instance of an ALERT PRIORITY TYPE.
Alert Priority Type | Standard Resolution Hour Count | Indicates the standard maximum duration of time (in hours) that could pass prior to being resolved for an ALERT for this instance of an ALERT PRIORITY TYPE.
Alert Priority Type | Effective Date | The date and time this instance became active.
Alert Priority Type | Termination Date | The last date that an instance of ALERT PRIORITY TYPE was valid.
Alert Type Priority Type | Alert Priority Type ID | The unique system-generated identifier for this instance of an ALERT TYPE PRIORITY TYPE.
Alert Type Priority Type | Alert Type ID | The unique identifier for the specific ALERT TYPE related to this instance of an ALERT TYPE PRIORITY TYPE.
Alert Type Priority Type | Effective Date | The date and time this instance became active.
Alert Type Priority Type | Termination Date | The last date that an instance of ALERT TYPE PRIORITY TYPE was valid.
Alert Resolution Type | Alert Resolution Type ID | The unique system-generated identifier for this instance of an ALERT RESOLUTION.
Alert Resolution Type | Alert Resolution Type Name | The unique textual designation given to this instance of an ALERT RESOLUTION TYPE.
Alert Resolution Type | Alert Resolution Type Description | Text describing this instance of an ALERT RESOLUTION TYPE.
Alert Resolution Type | Effective Date | The date and time this instance became active.
Alert Resolution Type | Termination Date | The last date that an instance of ALERT RESOLUTION TYPE was valid.
Alert Resolution Type
Alert Resolution | Alert Resolution ID | The unique system-generated identifier for this instance of an ALERT RESOLUTION.
Alert Resolution | Alert Resolution Date Time | The date and time the ALERT was resolved.
Alert Resolution | Alert Resolution Type ID | The unique identifier for the specific ALERT RESOLUTION TYPE related to this instance of an ALERT RESOLUTION.
Alert Resolution | Resolved by Person Business Entity ID | The unique identifier for the specific PERSON that completed the entry of how the ALERT was resolved this instance of an ALERT RESOLUTION.
Alert Resolution | Alert Resolution Description | A user provided description for each instance of an ALERT RESOLUTION.
Alert Remediation | Alert Remediation ID | The unique system-generated identifier for this instance of an ALERT REMEDIATION.
Alert Remediation | Management Plant Facility ID | The unique identifier for the specific Management Plant for where this ALERT REMEDIATION could be used to resolve the ALERT. When this is blank, the ALERT REMEDIATION refers to the enterprise (Aera wide).
Alert Remediation | Alert Type ID | The unique identifier for the specific ALERt TYPE related to this instance of an ALERT REMEDIATION.
Alert Remediation | Remediation Sequence Number | The order in which this remediation should be considered amongst other ALERT REMEDIATION related to the same ALERT TYPE.
Alert Remediation | Remediation Description | The descriptive text used to explain this instance of an ALERT REMEDIATION.
Alert Remediation | Effective Date | The date and time this instance became active.
Alert Remediation | Termination Date | The last date that an instance of ALERT RESOLUTION TYPE was valid.
Alert Resolution Remediation | Alert Resolution Remediation ID | The unique system-generated identifier for this instance of an ALERT RESOLUTION REMEDIATION.
Alert Resolution Remediation | Alert Resolution ID | The unique identifier for the specific ALERT RESOLUTION related to this instance of an ALERT RESOLUTION REMEDIATION.
Alert Resolution Remediation | Alert Remediation ID | The unique identifier for the specific ALERT REMEDIATION related to this instance of an ALERT RESOLUTION REMEDIATION.
Alert Likely Cause | Alert Likely Cause ID | The unique system-generated identifier for this instance of an ALERT LIKELY CAUSE.
Alert Likely Cause | Alert Type ID | The unique identifier for the specific ALERt TYPE related to this instance of an ALERT LIKELY CAUSE.
Alert Likely Cause | Management Plant Facility ID | The unique identifier for the specific Management Plant for where this ALERT LIKELY CAUSE may occur. When this is blank, the ALERT LIKELY CAUSE refers to the enterprise (Aera wide).
Alert Likely Cause | Sequence Number | The order in which this the likely cause should be considered amongst other ALERT LIKELY CAUSEs related to the same ALERT TYPE.
Alert Likely Cause | Cause Description | The descriptive text used to explain this instance of an ALERT LIKELY CAUSE.
Alert Likely Cause | Effective Date | The date and time this instance became active.
Alert Likely Cause | Termination Date | The last date that an instance of ALERT RESOLUTION TYPE was valid.
Alert Likely Cause Remediation | Alert Likely Cause Remediation ID | The unique system-generated identifier for this instance of an ALERT LIKELY CAUSE REMEDIATION.
Alert Likely Cause Remediation | Alert Likely Cause ID | The unique identifier for the specific ALERT LIKELY CAUSE related to this instance of an ALERT LIKELY CAUSE REMEDIATION.
Alert Likely Cause Remediation | Alert Remediation ID | The unique identifier for the specific ALERT REMEDIATION related to this instance of an ALERT LIKELY CAUSE REMEDIATION.
Alert Likely Cause Remediation | Effective Date | The date and time this instance became active.
Alert Likely Cause Remediation | Termination Date | The last date that an instance of ALERT RESOLUTION TYPE was valid.
Alert Response Type | Alert Response Type ID | The unique system-generated identifier for this instance of an ALERT RESOLUTION TYPE.
Alert Response Type | Alert Response Type Name | The unique textual designation given to this instance of an ALERT RESPONSE TYPE.
Alert Response Type | Alert Response Type Description | Text describing this instance of an ALERT RESPONSE TYPE.
Alert Response Type | Effective Date | The date and time this instance became active.
Alert Response Type | Termination Date | The last date that an instance of ALERT_RESPONSE TYPE was valid.
Alert Process Type | Alert Process Type ID | The unique system-generated identifier for this instance of an ALERT PROCESS TYPE.
Alert Process Type | Alert Process Name | The unique textual designation given to this instance of an ALERT PROCESS TYPE.
Alert Process Type | Alert Process Description | Text describing this instance of an ALERT PROCESS TYPE.
Alert Process Type | Effective Date | The date and time this instance became active.
Alert Process Type | Termination Date | The last date that an instance of ALERT PROCESS TYPE was valid.
Alert Sub Type | Alert Sub Type ID | The unique system-generated identifier for this instance of an ALERT SUB TYPE.
Alert Sub Type | Alert Process Type ID | The unique identifier for the specific ALERT PROCESS related to this instance of an ALERT SUB TYPE.
Alert Sub Type | Facility Type Code | The unique code for the specific FACILITY TYPE related to this instance of an ALERT SUB TYPE.
Alert Sub Type | Material Type ID | The unique identifier for the specific MATERIAL TYPE related to this instance of an ALERT SUB TYPE.
Alert Sub Type | Completion Purpose Type Code | The unique code for the specific COMPLETION PURPOSE TYPE related to this instance of an ALERT SUB TYPE.
Alert Sub Type | Alert Sub Type Name | The unique textual designation given to this instance of an ALERT SUB TYPE.
Alert Sub Type | Alert Sub Type Description | Text describing this instance of anALERT SUB TYPE.
Alert Sub Type | Effective Date | The date and time this instance became active.
Alert Sub Type | Termination Date | The last date that an instance of ALERT LOCATION TYPE was valid.
Alert Facility | Alert Facility ID | The unique system-generated identifier for this instance of an ALERT FACILITY.
Alert Facility | Alert ID | The unique identifier for the specific ALERT that reported this instance of an ALERT FACILITY.
Alert Facility | Facility ID | The unique identifier for the specific FACILITY that reported this instance of an ALERT FACILITY.
Alert Equipment Item | Alert Equipment Item ID | The unique system-generated identifier for this instance of an ALERT EQUIPMENT ITEM.
Alert Equipment Item | Equipment Item ID | The unique identifier for the specific EQUIPMENT ITEM that reported this instance of an ALERT EQUIPMENT ITEM.
Alert Equipment Item | Alert ID | The unique identifier for the specific ALERT that reported this instance of an ALERT EQUIPMENT ITEM.
Facility | Facility ID | The unique system-generated identifier for this instance of a FACILITY.
Facility | Criticality Type Code | The unique abbreviated textual representation for the specific Criticality Type related to this instance of FACILITY.
Facility | Facility Type Code | The unique abbreviated textual representation for the specific Facility Type related to this instance of FACILITY.
Equipment Item | Equipment Item ID | The unique system-generated identifier for this instance of a EQUIPMENT ITEM.
Equipment Item | Equipment Item Description | A textual description of a given ITEM.
Equipment Item | Equipment Item Serial Number | The manufacturer's number identifying the piece of equipment to the manufacturer.
Equipment Item | Construction Year | The year the EQUIPMENT ITEM was built.
Equipment Item | Construction Month | The month the EQUPMENT ITEM was built.
Equipment Item | Acquisition Date Time | The date the equipment item was acquired by the firm. If the equipment was acquired by a predecessor firm prior to the formation of the firm, it is the date the predecessor acquired the item. if the equipment is acquired in an acquisition of a property it is the date of the property acquisition.
Equipment Item | Disposition Date Time | The date and time the equipment was disposed.
Equipment Item | Controllable Indicator | Indicates that the equipment is subject to record and inventory control as determined by COPAS standards.
Equipment Item | Detailable Indicator | Indicates that the equipment is Controllable equipment which is required to be inventoried as part of Aera's asset verification policy.
Equipment Item | Incapable Of Safe Fluid Containment Indc | Indicates that an EQUIPMENT ITEM is not capable of safely containing fluids.
Equipment Item | Manufacturer ID | The unique identifier for the specific MANUFACTURER related to this instance of a EQUIPMENT ITEM.
Equipment Item | Facility ID | The unique identifier for the specific FACILITY related to this instance of a EQUIPMENT ITEM.
Equipment Item | Equipment Disposition Type ID | The unique identifier for the specific EQUIPMENT DISPOSITION TYPE related to this instance of a EQUIPMENT ITEM.
Worker | Worker Person Business Entity ID | The unique identifier for the specific BUSINESS ENTITY related to this instance of a WORKER.
Worker | Organization Business Entity ID | The unique identifier for the specific ORGANIZATION BUSINESS ENTITY related to this instance of a WORKER.
Worker | Worker Type Code ID | The unique identifier for the specific Work Schedule Type related to this instance of WORKER.
Worker | Worker Number | The unique identifier for the specific WORK EXEMPT TYPE related to this instance of a WORKER.
Worker | Period Work Schedule ID | The unique identifier for the specific PERIOD WORK SCHEDULE related to this instance of a WORKER.
Worker | Work Schedule Type Code | The unique abbreviated textual representation for the specific Work Schedule Type related to this instance of WORKER.

## Physical Model
Entity | Table | Table Definition
Alert | ALRT | An occurrence of a unfavorable condition of a Facility or Equipment Item that may require intervention in order to resume to full operation.
Alert Equipment Item | ALRT_EQPT_ITEM | Contains the specific Equipment Item(s) that are related to Alerts.
Alert Facility | ALRT_FAC | Contains the specific Facility(s) that are related to Alerts.
Alert Likely Cause | ALRT_LIKELY_CAUSE | The set of pre-defined likely causes that describe how an Alert with the specific Alert Type may have occurred.
Alert Likely Cause Remediation | ALRT_LIKELY_CAUSE_RMDTN | The link between a likely cause and it's remediation by Alert Type.
Alert Priority Type | ALRT_PRIO_TYPE | The valid set of classifications for how an Alert is ranked in importance.
Alert Process Type | ALRT_PRCS_TYPE | The operations process for which an Alert may occur and is being captured in the Operations Alert Manager application.
Alert Remediation | ALRT_RMDTN | The set of pre-defined remediations that describe how an Alert with the specific Alert Type was resolved.
Alert Resolution | N/A | Collapsed physically into Alert.
Alert Resolution Remediation | ALRT_RSLN_RMDTN | On Hold - Future.
Alert Resolution Type | ALRT_RSLN_TYPE | The valid set of classifications for how an Alert is resolved.
Alert Response | ALRT_RESP | Contains the information necessary to understand the reaction or work performed to Alerts.
Alert Response Type | ALRT_RESP_TYPE | The valid set of classifications of the reaction to an Alert.
Alert Sub Type | N/A | Collapsed physically into Alert.
Alert Trigger Type | ALRT_TRIG_TYPE | The valid set of classifications for how an Alert is reported.
Alert Triggering System | ALRT_TRIG_SYS | The valid list of system generated issues that create Alerts through automation.
Alert Type | ALRT_TYPE | The valid set of classifications for Alerts.
Alert Type Priority Type | ALRT_TYPE_PRIO_TYPE | The valid set of Alert Types and its assigned Priority Type. Some Alert Types may be associated to more than 1 Priority Type.
Completion Purpose Type | CMPL_PURP_TYPE | See Logical Defintion
Equipment Item | EQPT_ITEM | See Logical Defintion
Facility | FAC | See Logical Defintion
Facility Type | FAC_TYPE | See Logical Defintion
Management Plant | MGMT_PLNT | See Logical Defintion
Material Type | MATL_TYPE | See Logical Defintion
Worker | WRKR | See Logical Defintion

## Alert
Attribute Name | Alert ID | Alert Type Priority Type ID | Alert Create Date | Creator Person Business Entity ID | Alert Description | Alert Trigger Type ID | Alert Reported By Person Business Entity ID | Alert System Trigger Type ID | Alert Status Type ID | Alert Resolution Date Time | Alert Resolution Type ID | Resolved by Person Business Entity ID | Alert Resolution Description | Alert Note Text
Column Name
Attribute Characteristics | Primary Key, System Generated | Foreign Key, Required | Auto Populated with current date at time of creation. This CAN be back-dated | Required, Foreign Key | Free text, Required | Foreign Key, Required | Foreign Key, Optional, Either this attribute or Source System Notification ID must be filled in | Foreign Key, Optional, Either this attribute or Source Worker Person Business Entity ID must be filled in | Auto populated based on rules… default is Pending | Optional until resolved | Foreign Key, Optional until the resolved. | Foreign Key, Optional until the resolved. | Optional until resolved
Example | 1 |  | April 23, 2019 4:25pm |  | [Drive Pressure Average Deviation %] < 0.95 (Example from definition of rule) | 402 - System |  | 501 - PI |  | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID
Example | 2 |  | April 22, 2019 3:15pm |  | Groupline Flowrate Average Deviation %< ((Manifold Number of Operational In-Service Wells- 1) / Manifold Number of Operational In-Service Wells) or Groupline Flowrate Average Deviation %> ((Manifold Number of Operational In-Service Wells+ 1) / Manifold Number of Operational In-Service Wells) | 402 - System |  | 501 - PI |  | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID
Example | 3 |  | April 23, 2019 3:00pm | 11111111 (John Doe) | Operator walking through steam generators noticed that the Wheatley pump at Steam Generator has leaky seal | 401 - Person | 11111111 (John Doe) |  |  | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Create notification and work order
Example | 4 |  | April 23, 2019 3:00pm | 11111111 (John Doe) | PI + SCADA trends showed instability inflow into plant | 401 - Person | 11111111 (John Doe) |  |  | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Turned-off equipment and lockout energy sources
Example | 5 |  | April 23, 2019 3:00pm | 11111111 (John Doe) | While driving CALSO producer string Operator noticed steam injector well had large, active leak | 401 - Person | 11111111 (John Doe) |  |  | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Operator repaired in field
Example | 6 |  | April 23, 2019 3:00pm | 11111111 (John Doe) | Crew identified leaky seal on wellhead - indicates active gas leak | 401 - Person | 11111111 (John Doe) |  |  | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Created notification and work order
Example | 7 |  | April 23, 2019 3:00pm |  | FWKO level is very high, lift kill imminent | 402 - System |  | 502 - SCADA |  | April 23, 2019 3:00pm | 801 - Returned to Service | N/A |  | can a system resolve an Alert?
Example | 8 |  | April 23, 2019 3:00pm |  | Suction pressure to MPPs increasing indicating surge of gross, worn pump, or control issue | 402 - System |  | 502 - SCADA |  | April 23, 2019 3:00pm | 801 - Returned to Service | N/A |  | can a system resolve an Alert?

## Alert Response
Attribute Name | Alert Response ID | Alert ID | Response Type ID | Response Creator Business Entity ID | Response Create Date Time | Response Text | PM Number | Network Number | Network Activity Number
Attribute Characteristics | Primary Key, System Generated | Auto populated based on the Alert the response was created for. | Required | Auto Populated, to the person logged into the system at time of creation | Auto Populated with current date at time of creation. This CAN be back-dated | Free text | Optional | Optional | Optional
Example | 701
Example | 702
Example | 703
Example | 704
Example | 705
Example | 706
Example | 707
Example | 708

## Alert Facility
Attribute Name | Alert Facility ID | Alert ID | Facility ID
Attribute Characteristics | Primary Key Auto Generate | Foreign Key, Required | Foreign Key, Required
Example | 1001
Example | 1002
Example | 1003
Example | 1004
Example | 1005
Example | 1006
Example | 1007
Example | 1008

## Alert Equipment Item
Attribute Name | Alert Equipment Item ID | Alert ID | Equipment Item ID
Attribute Characteristics | Primary Key Auto Generate | Foreign Key, Required | Foreign Key, Required
Example | 1101
Example | 1102
Example | 1103
Example | 1104
Example | 1105
Example | 1106
Example | 1107
Example | 1108

## Alert Type
Attribute Name | Alert Type ID | Alert Type Name | Alert Type Description | Alert Process Type ID | Process Type Name | Facility Type Code | Management Plant Facility ID | Alert Priority Type ID | Alert Priority Name | Effective Date | Termination Date
Attribute Characteristics | Primary Key, System Generated | Required, must be unique | Free text description, Required | Foreign Key, Required | Displayed only to help in the ease of understanding the data | Foreign Key, optional |  | Foreign Key to Alert Priorty Type, Required | Displayed only to help in the ease of understanding the data | Auto Populated with current date at time of creation. | Not Required. Only enter when the type is no longer active.
Column Name | ALRT_TYPE_ID | ALRT_TYPE_NME | ALRT_TYPE_DESC | ALRT_PRCS_TYPE_ID | ALRT_PRCS_TYPE_NME | FAC_TYPE_CDE | MGMT_PLNT_FAC_ID | ALRT_DFLT_PRIO_TYPE_ID | ALRT_PRIO_TYPE_NME | EFTV_DTE | TERM_DTE
| 21 | Drive Pressure Average Deviation Alert | WHEN [Drive Pressure Average Deviation %] < 0.95 OR [Drive Pressure Average Deviation %] > 1.05 | 2 | Steam Injection | MFLD | NULL | 3 | Minor | 2019-06-06 | NULL
| 25 | Tubing Pressure Average Deviation Alert | WHEN [Tubing Pressure Average Deviation %] < 0.95 OR [Tubing Pressure Average Deviation %] > 1.05 | 2 | Steam Injection | CMPL | NULL | 3 | Minor | 2019-06-06 | NULL
| 26 | Operational Conformance Alert | WHEN [Operational Conformance %] < 0.90 OR [Operational Conformance %] > 1.10 | 2 | Steam Injection | CMPL | NULL | 3 | Minor | 2019-06-06 | NULL
| 27 | Engineering Conformance Alert | WHEN [<Path>¦Lego Data¦Constrained Target Value] = TRUE AND ( [Engineering Conformance %] < 0.90 OR [Engineering Conformance %] > 1.10 ) | 2 | Steam Injection | STGN | NULL | 3 | Minor | 2019-06-06 | NULL
| 28 | Strainer DP Average Deviation Alert | WHEN [Strainer DP Average Deviation %] < 0.95 OR [Strainer DP Average Deviation %] > 1.05 | 2 | Steam Injection | FWKO | NULL | 3 | Minor | 2019-06-06 | NULL
| 29 | Strainer DP High Alert | WHEN [<Path>¦Differential Pressure] > 10 | 2 | Steam Injection | CMPL | NULL | 1 | Critical | 2019-06-06 | NULL
| 30 | Regulatory Upper Limit Alert | WHEN [<Path>¦Process Data¦Tubing Pressure] > ( [<Path>¦Lego Data¦Regulatory Wellhead Tubing Pressure Upper Limit] – 50 ) | 2 | Steam Injection | CMPL | NULL | 1 | Critical | 2019-06-06 | NULL
| 31 | Choke Critical Pressure Ratio Alert | WHEN [Choke Critical Pressure Ratio] > 0.55 | 2 | Steam Injection | CMPL | NULL | 3 | Minor | 2019-06-06 | NULL
| 32 | Groupline Pressure Average Deviation Alert | Groupline Pressure Average Deviation % < 0.95 or Groupline Pressure Average Deviation % > 1.05 | 3 | Production Monitoring | CMPL | NULL | 4 | Warning | 2019-06-06 | NULL
| 33 | Inferred Production Average Deviation Alert | Inferred Production Average Deviation %< 0.95 or Inferred Production Average Deviation %> 1.05 | 3 | Production Monitoring | CMPL | NULL | 2 | Major | 2019-06-06 | NULL
| 34 | Flowline Temperature Average Deviation Alert | Flowline Temperature Average Deviation %< 0.95 or Flowline Temperature Average Deviation %> 1.05 | 3 | Production Monitoring | CMPL | NULL | 2 | Major | 2019-06-06 | NULL
| 35 | Casing Temperature Average Deviation Alert | Casing Temperature Average Deviation %< 0.95 or Casing Temperature Average Deviation %> 1.05 | 3 | Production Monitoring | CMPL | NULL | 3 | Minor | 2019-06-06 | NULL
| 36 | Well Test Gross Volume Alert | Current test volume/ previous test volume <0.90 or >1.10 | 3 | Production Monitoring | CMPL | NULL | 2 | Major | 2019-06-06 | NULL
| 37 | Communication Alert | Good Communication Percent < 0.95 | 3 | Production Monitoring | CMPL | NULL | 2 | Major | 2019-06-06 | NULL
| 38 | Current XSPOC Alarm Alert | Artificial lift data <none> Current Alarms is not null | 3 | Production Monitoring | CMPL | NULL | 2 | Major | 2019-06-06 | NULL
| 39 | Feedwater Pump Suction Average Deviation Alert | (10 min rolling average of Tag 5/ 3 hr rolling average of Tag 5) < 0.9 or (10 min rolling average of Tag 5/ 3 hr rolling average of Tag 5) ) > 1.1 | 2 | Steam Injection | STGN | NULL | 2 | Major | 2019-06-06 | NULL
| 40 | Steam Pressure Average Deviation Alert | (10 min rolling average of Tag E/ 3hr rolling average of Tag E) < 0.9 or (10 min rolling average of Tag E/ 3hr rolling average of Tag E) > 1.1 | 2 | Steam Injection | STGN | NULL | 3 | Minor | 2019-06-06 | NULL
| 41 | Burner Stack Temperature Average Deviation Alert | (10 min rolling average of Tag L/ 3 hr average of Tag L) < 0.9 or (10 min rolling average of Tag L/ 3 hr average of Tag L) > 1.1 | 2 | Steam Injection | STGN | NULL | 3 | Minor | 2019-06-06 | NULL
| 42 | Blower VFD Speed Average Deviation Alert | (10 min rolling average of Tag M/ 3 hr rolling average of Tag M) < 0.9 or (10 min rolling average of Tag M/ 3 hr rolling average of Tag M) > 1.1 | 2 | Steam Injection | STGN | NULL | 2 | Major | 2019-06-06 | NULL
| 43 | Generator Delta Pressure Average Deviation Alert | [(Tag 11 - Tag 38) / (Tag 12 - Tag 39)] < 0.9 or [(Tag 11 - Tag 38) / (Tag 12 - Tag 39)] > 1.1 | 2 | Steam Injection | STGN | NULL | 2 | Major | 2019-06-06 | NULL
| 44 | Feedwater Rate Setpoint Alarm | ABS(Tag A - Tag K) > 5 gpm | 2 | Steam Injection | STGN | NULL | 2 | Major | 2019-06-06 | NULL
| 45 | Low Steam Quality Alert | Tag H < Tag J | 2 | Steam Injection | STGN | NULL | 3 | Minor | 2019-06-06 | NULL
| 46 | High Steam Quality Alert | Tag H > (Tag J + 4) | 2 | Steam Injection | STGN | NULL | 2 | Major | 2019-06-06 | NULL
| 47 | O2 Setpoint Alert | Tag S >1.1*Tag T or Tag S < 0.9*Tag T | 2 | Steam Injection | STGN | NULL | 2 | Major | 2019-06-06 | NULL
| 48 | Fuel Gas Header Pressure Average Deviation Alert | Tag 86 < 0.9 or Tag 86 > 1.1 | 2 | Steam Injection | STGN | NULL | 1 | Critical | 2019-06-06 | NULL
| 49 | Generator Efficiency Average Deviation Alert | Tag 52 < 0.9 or Tag 52 > 1.1 | 2 | Steam Injection | STGN | NULL | 3 | Minor | 2019-06-06 | NULL
| 50 | High BSW | BSW > 40% | 5 | FWKO | FWKO | NULL | 3 | Minor | 2019-06-06 | NULL
| 51 | High BSW for 5 min | BSW > 40% for 5 straight minutes | 5 | FWKO | FWKO | NULL | 3 | Minor | 2019-06-06 | NULL
| 52 | Vessel Press Deviation Minor Alert | Tag 12 < .95 or Tag 12 > 1.05 | 5 | FWKO | FWKO | NULL | 2 | Major | 2019-06-06 | NULL
| 53 | Vessel Press Deviation Major Alert | Tag 12 < .90 or Tag 12 > 1.10 | 5 | FWKO | FWKO | NULL | 2 | Major | 2019-06-06 | NULL
| 54 | High vessel level alert | Tag 13 > X' (Luke to pull out of SCADA) | 5 | FWKO | FWKO | NULL | 1 | Critical | 2019-06-06 | NULL
| 55 | Critical high vessel level alert | Tag 13 > X' (Luke to pull out of SCADA) | 5 | FWKO | FWKO | NULL | 2 | Major | 2019-06-06 | NULL
| 56 | Interface level deviation alert | Tag 18 > 0.5' from Tag 23 | 5 | FWKO | FWKO | NULL | 3 | Minor | 2019-06-06 | NULL
| 57 | Vessel Temp Deviation Alert | Tag 27 < .95 or Tag 27 > 1.05 | 5 | FWKO | FWKO | NULL | 3 | Minor | 2019-06-06 | NULL
| 58 | CPMS Temp Deviation Alert | Tag 31 < .95 or Tag 31 > 1.05 | 5 | FWKO | FWKO | NULL | 3 | Minor | 2019-06-06 | NULL
| 59 | Comp Oil Rate Deviation to Yesterday | Tag 37 < .95 or Tag 37 > 1.05 All the manifolds rates should add up to the FWKO if that deviates the alert should trigger | 5 | FWKO | FWKO | NULL | 2 | Major | 2019-06-06 | NULL
| 60 | Comp Oil Rate Deviation | Tag 36 < .95 or Tag 36 > 1.05 | 5 | FWKO | FWKO | NULL | 3 | Minor | 2019-06-06 | NULL
| 61 | High BSW Standard Deviation | BSW< 24HR avg BSW - (tag 38*1.5) or BSW > 24HR avg BSW + (tag 38*1.5) | 5 | FWKO | FWKO | NULL | 2 | Major | 2019-06-06 | NULL
| 62 | Choke Differential Pressure Average Deviation Alert | WHEN [Choke Differential Average Deviation %] < 0.95 OR [Choke Differential Average Deviation %] > 1.05 | 2 | Steam Injection | MFLD | NULL | 2 | Major | 2019-06-06 | NULL
| 63 | Choke Differential Pressure Average Deviation Alert | WHEN [Choke Differential Average Deviation %] < 0.95 OR [Choke Differential Average Deviation %] > 1.05 | 2 | Steam Injection | MFLD | NULL | 2 | Major | 2019-06-06 | NULL
| 64 | Load Span Average Deviation Alert | NULL | 3 | Production Monitoring | CMPL | NULL | 3 | Minor | 2019-06-06 | NULL
| 65 | Fuel Gas Pressure Average Deviation Alert | NULL | 2 | Steam Injection | STGN | NULL | 3 | Minor | 2019-06-06 | NULL
| 66 | Total Softwater Flow - Gen Setting Feedwater Sum Deviation Alert | Tag 58 < 0.9 or Tag 58 > 1.1 | 2 | Steam Injection | STGN | NULL | 1 | Critical | 2019-06-06 | NULL
| 67 | Groupline Capacity Average Deviation Alert | Groupline Capacity Average Deviation %< ((Manifold Number of Operational In-Service Wells - 1) / Tag 33) or Groupline Capacity Average Deviation %> ((Manifold Number of Operational In-Service Wells - 1) / Tag 33) | 3 | Production Monitoring | CMPL | NULL | 2 | Major | 2019-06-06 | NULL
| 68 | Groupline Flowrate Average Deviation Alert | Groupline Flowrate Average Deviation %< ((Manifold Number of Operational In-Service Wells- 1) / Manifold Number of Operational In-Service Wells) or Groupline Flowrate Average Deviation %> ((Manifold Number of Operational In-Service Wells+ 1) / Manifold Number of Operational In-Service Wells) | 3 | Production Monitoring | CMPL | NULL | 2 | Major | 2019-06-06 | NULL
| 73 | Feedwater Rate Average Deviation Alert | \\BKPIAFSRV02\Aera Energy\Management Plant\Belridge\Steam Generator\Gen126¦Feedwater¦Rates and Volumes¦Feedwater Rate (10 minute rolling average) < 0.9 or \\BKPIAFSRV02\Aera Energy\Management Plant\Belridge\Steam Generator\Gen126¦Feedwater¦Rates and Volumes¦Feedwater Rate (3 day rolling average) > 1.1\\BKPIAFSRV02\Aera Energy\Management Plant\Belridge\Steam Generator\Gen126¦Feedwater¦Rates and Volumes¦Feedwater Rate (10 minute rolling average) < 0.9 or \\BKPIAFSRV02\Aera Energy\Management Plant\Belridge\Steam Generator\Gen126¦Feedwater¦Rates and Volumes¦Feedwater Rate (3 day rolling average) > 1.1 | 2 | Steam Injection | STGN | NULL | 4 | Warning | 2019-06-06 | NULL
| 74 | Feedwater Rate Average Deviation Alert | \\BKPIAFSRV02\Aera Energy\Management Plant\Belridge\Steam Generator\Gen126¦Feedwater¦Rates and Volumes¦Feedwater Rate (10 minute rolling average) < 0.9 or \\BKPIAFSRV02\Aera Energy\Management Plant\Belridge\Steam Generator\Gen126¦Feedwater¦Rates and Volumes¦Feedwater Rate (3 day rolling average) > 1.1 | 2 | Steam Injection | STGN | NULL | 4 | Warning | 2019-06-06 | NULL
| 75 | Steam Injection Operator Defined | This alert was created by an operator. See the Alert Description for details. | 2 | Steam Injection | NULL | NULL | 3 | Minor | 2019-06-10 11:12 | NULL
| 76 | Production Monitoring Operator Defined | This alert was created by an operator. See the Alert Description for details. | 3 | Production Monitoring | NULL | NULL | 3 | Minor | 2019-06-10 11:15 | NULL
| 77 | Steam Generation Operator Defined | This alert was created by an operator. See the Alert Description for details. | 4 | Steam Generation | NULL | NULL | 3 | Minor | 2019-06-10 11:16 | NULL
| 78 | FWKO Operator Defined | This alert was created by an operator. See the Alert Description for details. | 5 | FWKO | NULL | NULL | 3 | Minor | 2019-06-10 11:16 | NULL

## Alert Status Type
Attribute Name | Alert Status Type ID | Alert Status Type Name | Alert Status Type Description | Effective Date | Termination Date
Attribute Characteristics | Primary Key, System Generated | Required, must be unique | Required | Auto Populated with current date at time of creation. | Not Required. Only enter when the type is no longer active.
Column Name | ALRT_STAT_TYPE_ID | ALRT_STAT_TYPE_NME | ALRT_STAT_TYPE_DESC | EFTV_DTE | TERM_DTE
| 1 | Pending | Alert has not been viewed. | 2019-06-06 17:37
| 2 | In-Progress | Alert has at least 1 response and it is not resolved. | 2019-06-06 17:37
| 3 | Resolved | Alert has been resolved. | 2019-06-06 17:37

## Alert Process Type
Attribute Name | Alert Process Type ID | Alert Process Type Name | Alert Process Type Description | Effective Date | Termination Date
Attribute Characteristics | Primary Key, System Generated | Required, Unique | Required | Auto Populated with current date at time of creation. | Not Required. Only enter when the type is no longer active.
Column Name | ALRT_PRCS_TYPE_ID | ALRT_PRCS_TYPE_NME | ALRT_PRCS_TYPE_DESC | EFTV_DTE | TERM_DTE
| 2 | Steam Injection | The process of injecting steam into the ground. | 2019-05-28 17:15
| 3 | Production Monitoring | The process of extracting oil from the ground. | 2019-05-28 17:15
| 4 | Steam Generation | The process of making steam. | 2019-05-28 17:15
| 5 | FWKO | The process of separating oil from water and gas. | 2019-05-28 17:15

## Alert Priority Type
Attribute Name | Alert Priority Type ID | Alert Priority Type Name | Alert Priority Type Description | Standard Acknowledgement Hour Count | Standard Resolution Hour Count | Effective Date | Termination Date
Attribute Characteristics | Primary Key, System Generated | Required, must be unique | Free text description, Required | Required | Required | Auto Populated with current date at time of creation. | Not Required. Only enter when the type is no longer active.
Column Name | ALRT_PRIO_TYPE_ID | ALRT_PRIO_TYPE_NME | ALRT_PRIO_TYPE_DESC | STD_AKWLGMT_HOUR_CNT | STD_RSLN_HOUR_CNT | EFTV_DTE | TERM_DTE
Example | 1 | Critical | The condition that triggered the Alert should be resolved immediately. | 3 | 3 | 2019-05-28 17:22 | NULL
Example | 2 | Major | The condition that triggered the Alert should be resolved within a day. | 24 | 24 | 2019-05-28 17:23 | NULL
Example | 3 | Minor | The condition that triggered the Alert should be acknowledged within a day and resolved with 3 days. | 24 | 72 | 2019-05-28 17:23 | NULL
Example | 4 | Warning | The condition that triggered the Alert is a warning and should be closely monitored. | 72 | NULL | 2019-05-28 17:24 | NULL
Example | 5 | Information | The condition that triggered the Alert is only informational. | 72 | NULL | 2019-05-28 17:24 | NULL

## Alert Trigger Type
Attribute Name | Alert Trigger Type ID | Alert Trigger Type Name | Alert Trigger Type Description | Effective Date | Termination Date
Attribute Characteristics | Primary Key, System Generated | Required, must be unique | Free text description, Required | Auto Populated with current date at time of creation. | Not Required. Only enter when the type is no longer active.
Column Name | ALRT_TRIG_TYPE_ID | ALRT_TRIG_TYPE_NME | ALRT_TRIG_TYPE_DESC | EFTV_DTE | TERM_DTE
Example 1 | 1 | Person | The trigger was generated by an individual that observed a an unfavorable condition. | 43613.7302 | NULL
Example 2 | 2 | System | The trigger was generated by a system that alerted that an unfavorable conditon occurred or may occur. | 43613.7302 | NULL

## Alert Triggering System
Need to be completed before loading
Attribute Name | Alert Triggering System ID | Alert Triggering System Name | Alert Triggering System Description | Effective Date | Termination Date
Attribute Characteristics | Primary Key, System Generated | Required, must be unique | Free text description, Required | Auto Populated with current date at time of creation. | Not Required. Only enter when the type is no longer active.
Column Name | ALRT_TRIG_SYS_ID | ALRT_TRIG_SYS_NME | ALRT_TRIG_SYS_DESC | EFTV_DTE | TERM_DTE
| 5 | PI | OSI PI | 2019-06-04 | NULL
| 6 | SCADA | Includes Ignition, WonderWare and xSpoc | 2019-06-04 | NULL

## Alert Response Type
Attribute Name | Response Type ID | Response Type Name | Response Type Description | Effective Date | Termination Date
Attribute Characteristics | Primary Key, System Generated | Required, must be unique | Free text description, Required | Auto Populated with current date at time of creation. | Not Required. Only enter when the type is no longer active.
Column Name | ALRT_RESP_TYPE_ID | ALRT_RESP_TYPE_NME | ALRT_RESP_TYPE_DESC | EFTV_DTE | TERM_DTE
| 1 | Notified Operator | An operator was notificed to inspect the condition. | 2019-05-28 17:40 | NULL
| 2 | Notified Engineer | An engineer was notificed about the condition. | 2019-05-28 17:40 | NULL
| 3 | Created Work Order | A work order was create to ….. | 2019-05-28 17:40 | NULL

## Alert Resolution Type
Attribute Type | Alert Resolution Type ID | Alert Resolution Type Name | Alert Resolution Type Description | Effective Date | Termination Date
Attribute Characteristics | Primary Key, System Generated | Required, must be unique | Free text description, Required | Auto Populated with current date at time of creation. | Not Required. Only enter when the type is no longer active.
Column Name | ALRT_RSLN_TYPE_ID | ALRT_RSLN_TYPE_NME | ALRT_RSLN_TYPE_DESC | EFTV_DTE | TERM_DTE
| 1 | Returned to Service | Resolution corrected the condition and the equipment is fully operational. | 2019-05-28 17:44 | NULL
| 2 | Taken Out of Service | Resolution did not corrected the condition and the equipment was taken out of service. | 2019-05-28 17:44 | NULL
| 3 | False Alert - Bad Data | The alert was generated as a result of bad data. | 2019-05-28 17:44 | NULL
| 4 | False Alert - Bad Logic | The alert was generated as a result of bad logic. | 2019-05-28 17:44 | NULL
| 5 | No Intervention | No intervention was required and the equipment is fully operational. | 2019-05-28 17:44 | NULL
| 6 | Duplicate Alert | No action required | 2019-06-05 | NULL

## Event Resolution (hidden)
Atrribute Name | Event Resolution ID | Event Resolution Date Time | Event Resolution Type ID | Resolved by Person Business Entity ID | Event Resolution Description
Attribute Characteristics | Primary Key Auto Generate | Auto Populated with current date at time of creation. | Foreign Key, Required | Foreign Key, Required | This value will always be unique across all event types, Not Null
Example | 901 | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Choke Differential Pressure Average Deviation Alert: Check for plugged choke or other plugged surface equipment (check pressure and temperature upstream and downstream of choke, compare to steam table)
Example | 902 | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Groupline Flowrate Average Deviation Alert: Check to see if maintenance activity is ongoing in the area
Example | 903 | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Create notification and work order
Example | 904 | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Turn-off equipment and lockout energy sources
Example | 905 | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Operator repair in field
Example | 906 | April 23, 2019 3:00pm | 801 - Returned to Service | Aera Personnel ID | Create notification and work order
Example | 907 | April 23, 2019 3:00pm | 801 - Returned to Service | N/A | SCADA driven control action (there are tons of these) | can a system resxolve an event?
Example | 908 | April 23, 2019 3:00pm | 801 - Returned to Service | N/A | SCADA driven control action (there are tons of these) | can a system resxolve an event?